## Blank 2 Alarm Set-Point C&E
Blank Customer Matrix Template (2 Alarm Set-Points per channel)
To Be Used by Customer for Logic Template
|  |  |  | R1 | R2 | R3 | R4 | R5 | R6 | R7 | R8 | R9 | R10 | R11 | R12 | R13 | R14 | R15 | R16 | R17 | R18 | R19 | R20 | R21 | R22 | R23 | R24 | R25 | R26 | R27 | R28 | R29 | R30 | R31 | R32 | R33 | R34 | R35 | R36 | R37 | R38 | R39 | R40 | R41 | R42 | R43 | R44 | R45 | R46 | R47 | R48 | R49 | R50 | R51 | R52 | R53 | R54 | R55 | R56 | R57 | R58 | R59 | R60 | R61 | R62 | R63 | R64
| Channel/Detector Info | Tag Number | Location | Common Alarm | Common Fault | R3 | R4 | Panel Horn | R6 | R7 | R8 | R9 | R10 | R11 | R12 | R13 | R14 | R15 | R16 | R17 | R18 | R19 | R20 | R21 | R22 | R23 | R24 | R25 | R26 | R27 | R28 | R29 | R30 | R31 | R32 | R33 | R34 | R35 | R36 | R37 | R38 | R39 | R40 | R41 | R42 | R43 | R44 | R45 | R46 | R47 | R48 | R49 | R50 | R51 | R52 | R53 | R54 | R55 | R56 | R57 | R58 | R59 | R60 | R61 | R62 | R63 | R64
| Channel 1, A1 Alarm | CH01 | Location 1 | X |  |  |  | X
| Channel 1, A3 Alarm |  | Location 1 | X |  |  |  | X
| Channel 1, Fault |  | Location 1 |  | X |  |  | X
| Channel 2, A1 Alarm | CH02 | Location 2 | X |  |  |  | X
| Channel 2, A3 Alarm |  | Location 2 | X |  |  |  | X
| Channel 2, Fault |  | Location 2 |  | X |  |  | X
| Channel 3, A1 Alarm | CH03 | Location 3 | X |  |  |  | X
| Channel 3, A3 Alarm |  | Location 3 | X |  |  |  | X
| Channel 3, Fault |  | Location 3 |  | X |  |  | X
| Channel 4, A1 Alarm | CH04 | Location 4 | X |  |  |  | X
| Channel 4, A3 Alarm |  | Location 4 | X |  |  |  | X
| Channel 4, Fault |  | Location 4 |  | X |  |  | X
| Channel 5, A1 Alarm | CH05 | Location 5 | X |  |  |  | X
| Channel 5, A3 Alarm |  | Location 5 | X |  |  |  | X
| Channel 5, Fault |  | Location 5 |  | X |  |  | X
| Channel 6, A1 Alarm | CH06 | Location 6 | X |  |  |  | X
| Channel 6, A3 Alarm |  | Location 6 | X |  |  |  | X
| Channel 6, Fault |  | Location 6 |  | X |  |  | X
| Channel 7, A1 Alarm | CH07 | Location 7 | X |  |  |  | X
| Channel 7, A3 Alarm |  | Location 7 | X |  |  |  | X
| Channel 7, Fault |  | Location 7 |  | X |  |  | X
| Channel 8, A1 Alarm | CH08 | Location 8 | X |  |  |  | X
| Channel 8, A3 Alarm |  | Location 8 | X |  |  |  | X
| Channel 8, Fault |  | Location 8 |  | X |  |  | X
| Channel 9, A1 Alarm | CH09 | Location 9 | X |  |  |  | X
| Channel 9, A3 Alarm |  | Location 9 | X |  |  |  | X
| Channel 9, Fault |  | Location 9 |  | X |  |  | X
| Channel 10, A1 Alarm | CH10 | Location 10 | X |  |  |  | X
| Channel 10, A3 Alarm |  | Location 10 | X |  |  |  | X
| Channel 10, Fault |  | Location 10 |  | X |  |  | X
| Channel 11, A1 Alarm | CH11 | Location 11 | X |  |  |  | X
| Channel 11, A3 Alarm |  | Location 11 | X |  |  |  | X
| Channel 11, Fault |  | Location 11 |  | X |  |  | X
| Channel 12, A1 Alarm | CH12 | Location 12 | X |  |  |  | X
| Channel 12, A3 Alarm |  | Location 12 | X |  |  |  | X
| Channel 12, Fault |  | Location 12 |  | X |  |  | X
| Channel 13, A1 Alarm | CH13 | Location 13 | X |  |  |  | X
| Channel 13, A3 Alarm |  | Location 13 | X |  |  |  | X
| Channel 13, Fault |  | Location 13 |  | X |  |  | X
| Channel 14, A1 Alarm | CH14 | Location 14 | X |  |  |  | X
| Channel 14, A3 Alarm |  | Location 14 | X |  |  |  | X
| Channel 14, Fault |  | Location 14 |  | X |  |  | X
| Channel 15, A1 Alarm | CH15 | Location 15 | X |  |  |  | X
| Channel 15, A3 Alarm |  | Location 15 | X |  |  |  | X
| Channel 15, Fault |  | Location 15 |  | X |  |  | X
| Channel 16, A1 Alarm | CH16 | Location 16 | X |  |  |  | X
| Channel 16, A3 Alarm |  | Location 16 | X |  |  |  | X
| Channel 16, Fault |  | Location 16 |  | X |  |  | X
| Discrete Input 3 | DI3 | DI Inputs have no editable Location Text Box | X |  |  |  | X
| Discrete Input 4 | DI4 |  | X |  |  |  | X
| Discrete Input 5 | DI5 |  | X |  |  |  | X
| Discrete Input 6 | DI6 |  | X |  |  |  | X
| Discrete Input 7 | DI7 |  | X |  |  |  | X
| Discrete Input 8 | DI8 |  | X |  |  |  | X
|  | Notes: |  |  | Warnings: | bar: R6 R6 to R7 R7
|  | Relays 1, 2 & 5 are pre-programmed configurations with the following settings. R1 = Common Alarm, R2= Common Fault, R5= SENTRY io Buzzer. These three relays are non-adjustable, non-changeable. |  |  | These templates are provided to allow pre-planning of programming of the SENTRY io.
All configuratons should be validated by a full functional test after configuration is completed.
Relays 4, 5 and all relays 6 and above are all user configurable through the touchscreen wizard.
|  | Cause and Effect logic in the touchscreen wizard establishes "AND" relationships, and is assigned to individual relays above. These 'and" relationships are designated by an "X" |  |  | You can download a .csv file with your configuration after completing the set-up wizard, but this does not replace a full functional test.
8 Voting Zones are available and user assignable. These voting zones are labeled V1-V8, and can be configured with three different logical equations "2 of n", "3 of n", "OR gates
Tag Number and Location are user configurable descriptions
Relays 1-4 come preconfigured as dry contacts from the factory
Relays 5-8 come preconfigured from the factory as 24VDC powered contacts
Relay labels are user configurable

## Blank 3 Alarm Set-Point C&E
Blank Customer Matrix Template (3 Alarm Set-Points per channel)
To Be Used by Customer for Logic Template
|  |  |  | R1 | R2 | R3 | R4 | R5 | R6 | R7 | R8 | R9 | R10 | R11 | R12 | R13 | R14 | R15 | R16 | R17 | R18 | R19 | R20 | R21 | R22 | R23 | R24 | R25 | R26 | R27 | R28 | R29 | R30 | R31 | R32 | R33 | R34 | R35 | R36 | R37 | R38 | R39 | R40 | R41 | R42 | R43 | R44 | R45 | R46 | R47 | R48 | R49 | R50 | R51 | R52 | R53 | R54 | R55 | R56 | R57 | R58 | R59 | R60 | R61 | R62 | R63 | R64
| Channel/Detector Info | Tag Number | Location | Common Alarm | Common Fault | R3 | R4 | Panel Horn | R6 | R7 | R8 | R9 | R10 | R11 | R12 | R13 | R14 | R15 | R16 | R17 | R18 | R19 | R20 | R21 | R22 | R23 | R24 | R25 | R26 | R27 | R28 | R29 | R30 | R31 | R32 | R33 | R34 | R35 | R36 | R37 | R38 | R39 | R40 | R41 | R42 | R43 | R44 | R45 | R46 | R47 | R48 | R49 | R50 | R51 | R52 | R53 | R54 | R55 | R56 | R57 | R58 | R59 | R60 | R61 | R62 | R63 | R64
| Channel 1, A1 Alarm | CH01 | Location 1 | X |  |  |  | X
| Channel 1, A2 Alarm |  | Location 1 | X |  |  |  | X
| Channel 1, A3 Alarm |  | Location 1 | X |  |  |  | X
| Channel 1, Fault |  | Location 1 |  | X |  |  | X
| Channel 2, A1 Alarm | CH02 | Location 2 | X |  |  |  | X
| Channel 2, A2 Alarm |  | Location 2 | X |  |  |  | X
| Channel 2, A3 Alarm |  | Location 2 | X |  |  |  | X
| Channel 2, Fault |  | Location 2 |  | X |  |  | X
| Channel 3, A1 Alarm | CH03 | Location 3 | X |  |  |  | X
| Channel 3, A2 Alarm |  | Location 3 | X |  |  |  | X
| Channel 3, A3 Alarm |  | Location 3 | X |  |  |  | X
| Channel 3, Fault |  | Location 3 |  | X |  |  | X
| Channel 4, A1 Alarm | CH04 | Location 4 | X |  |  |  | X
| Channel 4, A2 Alarm |  | Location 4 | X |  |  |  | X
| Channel 4, A3 Alarm |  | Location 4 | X |  |  |  | X
| Channel 4, Fault |  | Location 4 |  | X |  |  | X
| Channel 5, A1 Alarm | CH05 | Location 5 | X |  |  |  | X
| Channel 5, A2 Alarm |  | Location 5 | X |  |  |  | X
| Channel 5, A3 Alarm |  | Location 5 | X |  |  |  | X
| Channel 5, Fault |  | Location 5 |  | X |  |  | X
| Channel 6, A1 Alarm | CH06 | Location 6 | X |  |  |  | X
| Channel 6, A2 Alarm |  | Location 6 | X |  |  |  | X
| Channel 6, A3 Alarm |  | Location 6 | X |  |  |  | X
| Channel 6, Fault |  | Location 6 |  | X |  |  | X
| Channel 7, A1 Alarm | CH07 | Location 7 | X |  |  |  | X
| Channel 7, A2 Alarm |  | Location 7 | X |  |  |  | X
| Channel 7, A3 Alarm |  | Location 7 | X |  |  |  | X
| Channel 7, Fault |  | Location 7 |  | X |  |  | X
| Channel 8, A1 Alarm | CH08 | Location 8 | X |  |  |  | X
| Channel 8, A2 Alarm |  | Location 8 | X |  |  |  | X
| Channel 8, A3 Alarm |  | Location 8 | X |  |  |  | X
| Channel 8, Fault |  | Location 8 |  | X |  |  | X
| Channel 9, A1 Alarm | CH09 | Location 9 | X |  |  |  | X
| Channel 9, A2 Alarm |  | Location 9 | X |  |  |  | X
| Channel 9, A3 Alarm |  | Location 9 | X |  |  |  | X
| Channel 9, Fault |  | Location 9 |  | X |  |  | X
| Channel 10, A1 Alarm | CH10 | Location 10 | X |  |  |  | X
| Channel 10, A2 Alarm |  | Location 10 | X |  |  |  | X
| Channel 10, A3 Alarm |  | Location 10 | X |  |  |  | X
| Channel 10, Fault |  | Location 10 |  | X |  |  | X
| Channel 11, A1 Alarm | CH11 | Location 11 | X |  |  |  | X
| Channel 11, A2 Alarm |  | Location 11 | X |  |  |  | X
| Channel 11, A3 Alarm |  | Location 11 | X |  |  |  | X
| Channel 11, Fault |  | Location 11 |  | X |  |  | X
| Channel 12, A1 Alarm | CH12 | Location 12 | X |  |  |  | X
| Channel 12, A2 Alarm |  | Location 12 | X |  |  |  | X
| Channel 12, A3 Alarm |  | Location 12 | X |  |  |  | X
| Channel 12, Fault |  | Location 12 |  | X |  |  | X
| Channel 13, A1 Alarm | CH13 | Location 13 | X |  |  |  | X
| Channel 13, A2 Alarm |  | Location 13 | X |  |  |  | X
| Channel 13, A3 Alarm |  | Location 13 | X |  |  |  | X
| Channel 13, Fault |  | Location 13 |  | X |  |  | X
| Channel 14, A1 Alarm | CH14 | Location 14 | X |  |  |  | X
| Channel 14, A2 Alarm |  | Location 14 | X |  |  |  | X
| Channel 14, A3 Alarm |  | Location 14 | X |  |  |  | X
| Channel 14, Fault |  | Location 14 |  | X |  |  | X
| Channel 15, A1 Alarm | CH15 | Location 15 | X |  |  |  | X
| Channel 15, A2 Alarm |  | Location 15 | X |  |  |  | X
| Channel 15, A3 Alarm |  | Location 15 | X |  |  |  | X
| Channel 15, Fault |  | Location 15 |  | X |  |  | X
| Channel 16, A1 Alarm | CH16 | Location 16 | X |  |  |  | X
| Channel 16, A2 Alarm |  | Location 16 | X |  |  |  | X
| Channel 16, A3 Alarm |  | Location 16 | X |  |  |  | X
| Channel 16, Fault |  | Location 16 |  | X |  |  | X
| Discrete Input 3 | DI3 | DI Inputs have no editable Location Text Box | X |  |  |  | X
| Discrete Input 4 | DI4 |  | X |  |  |  | X
| Discrete Input 5 | DI5 |  | X |  |  |  | X
| Discrete Input 6 | DI6 |  | X |  |  |  | X
| Discrete Input 7 | DI7 |  | X |  |  |  | X
| Discrete Input 8 | DI8 |  | X |  |  |  | X
|  | Notes: |  |  | Warnings: | bar: R6 R6 to R7 R7
|  | Relays 1, 2 & 5 are pre-programmed configurations with the following settings. R1 = Common Alarm, R2= Common Fault, R5= SENTRY io Buzzer. These three relays are non-adjustable, non-changeable. |  |  | These templates are provided to allow pre-planning of programming of the SENTRY io.
All configuratons should be validated by a full functional test after configuration is completed.
Relays 4, 5 and all relays 6 and above are all user configurable through the touchscreen wizard.
|  | Cause and Effect logic in the touchscreen wizard establishes "AND" relationships, and is assigned to individual relays above. These 'and" relationships are designated by an "X" |  |  | You can download a .csv file with your configuration after completing the set-up wizard, but this does not replace a full functional test.
8 Voting Zones are available and user assignable. These voting zones are labeled V1-V8, and can be configured with three different logical equations "2 of n", "3 of n", "OR gates
Tag Number and Location are user configurable descriptions
Relays 1-4 come preconfigured as dry contacts from the factory
Relays 5-8 come preconfigured from the factory as 24VDC powered contacts
Relay labels are user configurable

## Sample 3 Alarm Set-Point Config
Sample Matrix Below Assumes 3 Alarm Set-Points per channel
For Illustration of Possible Programming Options
[13 empty] | Voting Zone 1 | Voting Zone 2 | Voting Zone 3 |  |  |  | Voting Zone 4 |  | Voting Zone 5
|  |  |  | R1 | R2 | R3 | R4 | R5 | R6 | R7 | R8 | R9 | R10 | R11 | R12 | R13 | R14 | R15 | R16 | R17 | R18 | R19 | R20 | R21 | R22 | R23 | R24 | R25 | R26 | R27 | R28 | R29 | R30 | R31 | R32
| Channel/Detector Info | Tag Number | Location | Common Alarm | Common Fault | Tank Farm Alarm Horns (silenceable) | Tank Farm Strobes | Panel Horn | Tank A Shut-Off Valve | Tank B Shut-Off Valve | Tank C Shut-Off Valve | Tank D Shut-Off Valve | Voting any 3 Alarms, Tank Farm Shut-Down | Voting any 2 Tank Farm Evacuation Signal, | Or Gate, Common Alarm Tank Farm | Common Fault Tank Farm | Compressor Building Alarm Horn (silenceable) | Compressor Building Strobe Lights | Any 2 Compressor Building Shut-Down | Common Fire Compressor Building | Any 2 Confirmed Fire Compressor Building | Common Alarm Compressor Building | Common Fault Compressor Building | MCC Building HVAC Shut-Off | R22 | R23 | R23 | R25 | R26 | R27 | R28 | R29 | R30 | R31 | R32
| Channel 1, S4000CH A1 Alarm (20 LEL) | CH01 Combust | Tank Farm Tank A | X |  |  |  | X
| Channel 1, S4000CH A2 Alarm (25 LEL) |  | Tank Farm Tank A | X |  |  | X | X | [5 empty] | V2
| Channel 1, S4000CH A3 Alarm (40 LEL) |  | Tank Farm Tank A | X |  | X |  | X | X |  |  |  | V1
| Channel 1, S4000CH Fault |  | Tank Farm Tank A |  | X |  |  | X | [7 empty] | X
| Channel 2, S4000CH A1 Alarm (20 LEL) | CH02 Combust | Tank Farm Tank B | X |  |  |  | X
| Channel 2, S4000CH A2 Alarm (25 LEL) |  | Tank Farm Tank B | X |  |  | X | X | [5 empty] | V2
| Channel 2, S4000CH A3 Alarm (40 LEL) |  | Tank Farm Tank B | X |  | X |  | X |  | X |  |  | V1
| Channel 2, S4000CH Fault |  | Tank Farm Tank B |  | X |  |  | X | [7 empty] | X
| Channel 3, S4000CH A1 Alarm (20 LEL) | CH03 Combust | Tank Farm Tank C | X |  |  |  | X
| Channel 3, S4000CH A2 Alarm (25 LEL) |  | Tank Farm Tank C | X |  |  | X | X | [5 empty] | V2
| Channel 3, S4000CH A3 Alarm (40 LEL) |  | Tank Farm Tank C | X |  | X |  | X |  |  | X |  | V1
| Channel 3, S4000CH Fault |  | Tank Farm Tank C |  | X |  |  | X | [7 empty] | X
| Channel 4, S4000CH A1 Alarm (20 LEL) | CH04 Combust | Tank Farm Tank D | X |  |  |  | X
| Channel 4, S4000CH A2 Alarm (25 LEL) |  | Tank Farm Tank D | X |  |  | X | X | [5 empty] | V2
| Channel 4, S4000CH A3 Alarm (40 LEL) |  | Tank Farm Tank D | X |  | X |  | X |  |  |  | X | V1
| Channel 4, S4000CH Fault |  | Tank Farm Tank D |  | X |  |  | X | [7 empty] | X
| Channel 5, FL500 Flame Detector Alarm | CH05 Flame | Tank Farm NW Corner | X |  | X | X | X |  |  |  |  | V1 |  | V3
| Channel 5, FL500 Fault |  | Tank Farm NW Corner |  | X |  |  | X | [7 empty] | X
| Channel 6, FL500 Flame Detector Alarm | CH06 Flame | Tank Farm SE Corner | X |  | X | X | X |  |  |  |  | V1 |  | V3
| Channel 6, FL500 Fault |  | Tank Farm SE Corner |  | X |  |  | X | [7 empty] | X
| Channel 7, Spare | CH07 Spare | Location 7
| Channel 8, Ultima XIR A1 Alarm (10 LEL) | CH08 IR CH4 | Compressor Bldg South | X |  |  |  | X | [8 empty] | X
| Channel 8, Ultima XIR A2 Alarm (20 LEL) |  | Compressor Bldg South | X |  |  |  | X | [9 empty] | X
| Channel 8, Ultima XIR A3 Alarm (30 LEL) |  | Compressor Bldg South | X |  |  |  | X | [10 empty] | V4 |  |  | X
| Channel 8, Ultima XIR Fault |  | Compressor Bldg South |  | X |  |  | X | [14 empty] | X
| Channel 9, Ultima XIR A1 Alarm (10 LEL) | CH09 IR CH4 | Compressor Bldg Central | X |  |  |  | X | [8 empty] | X
| Channel 9, Ultima XIR A2 Alarm (20 LEL) |  | Compressor Bldg Central | X |  |  |  | X | [9 empty] | X
| Channel 9, Ultima XIR A3 Alarm (30 LEL) |  | Compressor Bldg Central | X |  |  |  | X | [10 empty] | V4 |  |  | X
| Channel 9, Ultima XIR Fault |  | Compressor Bldg Central |  | X |  |  | X | [14 empty] | X
| Channel 10, Ultima XIR A1 Alarm (10 LEL) | CH10 IR CH4 | Compressor Bldg North | X |  |  |  | X | [8 empty] | X
| Channel 10, Ultima XIR A2 Alarm (20 LEL) |  | Compressor Bldg North | X |  |  |  | X | [9 empty] | X
| Channel 10, Ultima XIR A3 Alarm (30 LEL) |  | Compressor Bldg North | X |  |  |  | X | [10 empty] | V4 |  |  | X
| Channel 10, Ultima XIR Fault |  | Compressor Bldg North |  | X |  |  | X | [14 empty] | X
| Channel 11, Ultima XIR A1 Alarm (10 LEL) | CH11 IR CH4 | Compressor Bldg Cellar | X |  |  |  | X | [8 empty] | X
| Channel 11, Ultima XIR A2 Alarm (20 LEL) |  | Compressor Bldg Cellar | X |  |  |  | X | [9 empty] | X
| Channel 11, Ultima XIR A3 Alarm (30 LEL) |  | Compressor Bldg Cellar | X |  |  |  | X | [10 empty] | V4 |  |  | X
| Channel 11, Ultima XIR Fault |  | Compressor Bldg Cellar |  | X |  |  | X | [14 empty] | X
| Channel 12, FL3100H Flame Detector Alarm | CH12 Flame | Compressor Bldg SW Corner | X |  |  |  | X | [8 empty] | X | X |  | X | V5 | X
| Channel 12, FL3100H Fault |  | Compressor Bldg SW Corner | X |  |  |  | X | [14 empty] | X
| Channel 13, FL3100H Flame Detector Alarm | CH13 Flame | Compressor Bldg SE Corner | X |  |  |  | X | [8 empty] | X | X |  | X | V5 | X
| Channel 13, FL3100HFault |  | Compressor Bldg SE Corner |  | X |  |  | X | [14 empty] | X
| Channel 14, FL3100H Flame Detector Alarm | CH14 Flame | Compressor Bldg NW Corner | X |  |  |  | X | [8 empty] | X | X |  | X | V5 | X
| Channel 14, FL3100H Fault |  | Compressor Bldg NW Corner | X |  |  |  | X | [14 empty] | X
| Channel 15, FL3100H Flame Detector Alarm | CH15 Flame | Compressor Bldg NE Corner | X |  |  |  | X | [8 empty] | X | X |  | X | V5 | X
| Channel 15, FL3100H Fault |  | Compressor Bldg NE Corner |  | X |  |  | X | [14 empty] | X
| Channel 16, IR400 A1 Alarm (5 LEL) | CH16 Combust | MCC Building HVAC inlet | X |  |  |  | X
| Channel 16, IR400 A2 Alarm (10 LEL) |  | MCC Building HVAC inlet | X |  |  |  | X | [15 empty] | X
| Channel 16, IR400 A3 Alarm (15 LEL) |  | MCC Building HVAC inlet | X |  |  |  | X
| Channel 16, IR400 Fault |  | MCC Building HVAC inlet |  | X |  |  | X
| Discrete Input 3 | Tank Farm ESD Button | DI Inputs have no editable Location Text Box | X |  |  |  | X |  |  |  |  | V1
| Discrete Input 4, | Compress or Bldg Strobes Button |  | X |  |  |  | X | [9 empty] | X
| Discrete Input 5, Spare | DI5
| Discrete Input 6, Spare | DI6
| Discrete Input 7, Spare | DI7
| Discrete Input 8, Spare | DI8
|  | Notes: |  |  | Warnings:
|  | Relays 1, 2 & 5 are pre-programmed configurations with the following settings. R1 = Common Alarm, R2= Common Fault, R5= SENTRY io Buzzer. These three relays are non-adjustable, non-changeable. |  |  | These templates are provided to allow pre-planning of programming of the SENTRY io.
All configuratons should be validated by a full functional test after configuration is completed.
Relays 4, 5 and all relays 6 and above are all user configurable through the touchscreen wizard.
|  | Cause and Effect logic in the touchscreen wizard establishes "AND" relationships, and is assigned to individual relays above. These 'and" relationships are designated by an "X" |  |  | You can download a .csv file with your configuration after completing the set-up wizard, but this does not replace a full functional test.
8 Voting Zones are available and user assignable. These voting zones are labeled V1-V8, and can be configured with three different logical equations "2 of n", "3 of n", "OR gates
Tag Number and Location are user configurable descriptions
Relays 1-4 come preconfigured as dry contacts from the factory
Relays 5-8 come preconfigured from the factory as 24VDC powered contacts
Relay labels are user configurable