## Sheet1
SENTRY io MODBUS ADDRESS LIST
| DISCRETE ALARMS |  | DISCRETE ALARMS
CHANNEL STATUS | MODBUS ADDRESS | CHANNEL STATUS | MODBUS ADDRESS
CHANNEL 1 A1 | 10001 | CHANNEL 9 A1 | 10081
CHANNEL 1 A2 | 10002 | CHANNEL 9 A2 | 10082
CHANNEL 1 A3 | 10003 | CHANNEL 9 A3 | 10083
CHANNEL 1 FAULT 1 (UNDER RANGE) | 10004 | CHANNEL 9 FAULT 1 (UNDER RANGE) | 10084
CHANNEL 1 FAULT 2 (UNDER RANGE) | 10005 | CHANNEL 9 FAULT 2 (UNDER RANGE) | 10085
CHANNEL 1 FAULT 3 (UNDER RANGE) | 10006 | CHANNEL 9 FAULT 3 (UNDER RANGE) | 10086
CHANNEL 1 FAULT 4 (UNDER RANGE) | 10007 | CHANNEL 9 FAULT 4 (UNDER RANGE) | 10087
CHANNEL 1 RESERVED 1 (FUTURE) | 10008 | CHANNEL 9 RESERVED 1 (FUTURE) | 10088
CHANNEL 1 RESERVED 2 (FUTURE) | 10009 | CHANNEL 9 RESERVED 2 (FUTURE) | 10089
CHANNEL 1 INHIBIT | 10010 | CHANNEL 9 INHIBIT | 10090
CHANNEL 2 A1 | 10011 | CHANNEL 10 A1 | 10091
CHANNEL 2 A2 | 10012 | CHANNEL 10 A2 | 10092
CHANNEL 2 A3 | 10013 | CHANNEL 10 A3 | 10093
CHANNEL 2 FAULT 1 (UNDER RANGE) | 10014 | CHANNEL 10 FAULT 1 (UNDER RANGE) | 10094
CHANNEL 2 FAULT 2 (UNDER RANGE) | 10015 | CHANNEL 10 FAULT 2 (UNDER RANGE) | 10095
CHANNEL 2 FAULT 3 (UNDER RANGE) | 10016 | CHANNEL 10 FAULT 3 (UNDER RANGE) | 10096
CHANNEL 2 FAULT 4 (UNDER RANGE) | 10017 | CHANNEL 10 FAULT 4 (UNDER RANGE) | 10097
CHANNEL 2 RESERVED 1 (FUTURE) | 10018 | CHANNEL 10 RESERVED 1 (FUTURE) | 10098
CHANNEL 2 RESERVED 2 (FUTURE) | 10019 | CHANNEL 10 RESERVED 2 (FUTURE) | 10099
CHANNEL 2 INHIBIT | 10020 | CHANNEL 10 INHIBIT | 10100
CHANNEL 3 A1 | 10021 | CHANNEL 11 A1 | 10101
CHANNEL 3 A2 | 10022 | CHANNEL 11 A2 | 10102
CHANNEL 3 A3 | 10023 | CHANNEL 11 A3 | 10103
CHANNEL 3 FAULT 1 (UNDER RANGE) | 10024 | CHANNEL 11 FAULT 1 (UNDER RANGE) | 10104
CHANNEL 3 FAULT 2 (UNDER RANGE) | 10025 | CHANNEL 11 FAULT 2 (UNDER RANGE) | 10105
CHANNEL 3 FAULT 3 (UNDER RANGE) | 10026 | CHANNEL 11 FAULT 3 (UNDER RANGE) | 10106
CHANNEL 3 FAULT 4 (UNDER RANGE) | 10027 | CHANNEL 11 FAULT 4 (UNDER RANGE) | 10107
CHANNEL 3 RESERVED 1 (FUTURE) | 10028 | CHANNEL 11 RESERVED 1 (FUTURE) | 10108
CHANNEL 3 RESERVED 2 (FUTURE) | 10029 | CHANNEL 11 RESERVED 2 (FUTURE) | 10109
CHANNEL 3 INHIBIT | 10030 | CHANNEL 11 INHIBIT | 10110
CHANNEL 4 A1 | 10031 | CHANNEL 12 A1 | 10111
CHANNEL 4 A2 | 10032 | CHANNEL 12 A2 | 10112
CHANNEL 4 A3 | 10033 | CHANNEL 12 A3 | 10113
CHANNEL 4 FAULT 1 (UNDER RANGE) | 10034 | CHANNEL 12 FAULT 1 (UNDER RANGE) | 10114
CHANNEL 4 FAULT 2 (UNDER RANGE) | 10035 | CHANNEL 12 FAULT 2 (UNDER RANGE) | 10115
CHANNEL 4 FAULT 3 (UNDER RANGE) | 10036 | CHANNEL 12 FAULT 3 (UNDER RANGE) | 10116
CHANNEL 4 FAULT 4 (UNDER RANGE) | 10037 | CHANNEL 12 FAULT 4 (UNDER RANGE) | 10117
CHANNEL 4 RESERVED 1 (FUTURE) | 10038 | CHANNEL 12 RESERVED 1 (FUTURE) | 10118
CHANNEL 4 RESERVED 2 (FUTURE) | 10039 | CHANNEL 12 RESERVED 2 (FUTURE) | 10119
CHANNEL 4 INHIBIT | 10040 | CHANNEL 12 INHIBIT | 10120
CHANNEL 5 A1 | 10041 | CHANNEL 13 A1 | 10121
CHANNEL 5 A2 | 10042 | CHANNEL 13 A2 | 10122
CHANNEL 5 A3 | 10043 | CHANNEL 13 A3 | 10123
CHANNEL 5 FAULT 1 (UNDER RANGE) | 10044 | CHANNEL 13 FAULT 1 (UNDER RANGE) | 10124
CHANNEL 5 FAULT 2 (UNDER RANGE) | 10045 | CHANNEL 13 FAULT 2 (UNDER RANGE) | 10125
CHANNEL 5 FAULT 3 (UNDER RANGE) | 10046 | CHANNEL 13 FAULT 3 (UNDER RANGE) | 10126
CHANNEL 5 FAULT 4 (UNDER RANGE) | 10047 | CHANNEL 13 FAULT 4 (UNDER RANGE) | 10127
CHANNEL 5 RESERVED 1 (FUTURE) | 10048 | CHANNEL 13 RESERVED 1 (FUTURE) | 10128
CHANNEL 5 RESERVED 2 (FUTURE) | 10049 | CHANNEL 13 RESERVED 2 (FUTURE) | 10129
CHANNEL 5 INHIBIT | 10050 | CHANNEL 13 INHIBIT | 10130
CHANNEL 6 A1 | 10051 | CHANNEL 14 A1 | 10131
CHANNEL 6 A2 | 10052 | CHANNEL 14 A2 | 10132
CHANNEL 6 A3 | 10053 | CHANNEL 14 A3 | 10133
CHANNEL 6 FAULT 1 (UNDER RANGE) | 10054 | CHANNEL 14 FAULT 1 (UNDER RANGE) | 10134
CHANNEL 6 FAULT 2 (UNDER RANGE) | 10055 | CHANNEL 14 FAULT 2 (UNDER RANGE) | 10135
CHANNEL 6 FAULT 3 (UNDER RANGE) | 10056 | CHANNEL 14 FAULT 3 (UNDER RANGE) | 10136
CHANNEL 6 FAULT 4 (UNDER RANGE) | 10057 | CHANNEL 14 FAULT 4 (UNDER RANGE) | 10137
CHANNEL 6 RESERVED 1 (FUTURE) | 10058 | CHANNEL 14 RESERVED 1 (FUTURE) | 10138
CHANNEL 6 RESERVED 2 (FUTURE) | 10059 | CHANNEL 14 RESERVED 2 (FUTURE) | 10139
CHANNEL 6 INHIBIT | 10060 | CHANNEL 14 INHIBIT | 10140
CHANNEL 7 A1 | 10061 | CHANNEL 15 A1 | 10141
CHANNEL 7 A2 | 10062 | CHANNEL 15 A2 | 10142
CHANNEL 7 A3 | 10063 | CHANNEL 15 A3 | 10143
CHANNEL 7 FAULT 1 (UNDER RANGE) | 10064 | CHANNEL 15 FAULT 1 (UNDER RANGE) | 10144
CHANNEL 7 FAULT 2 (UNDER RANGE) | 10065 | CHANNEL 15 FAULT 2 (UNDER RANGE) | 10145
CHANNEL 7 FAULT 3 (UNDER RANGE) | 10066 | CHANNEL 15 FAULT 3 (UNDER RANGE) | 10146
CHANNEL 7 FAULT 4 (UNDER RANGE) | 10067 | CHANNEL 15 FAULT 4 (UNDER RANGE) | 10147
CHANNEL 7 RESERVED 1 (FUTURE) | 10068 | CHANNEL 15 RESERVED 1 (FUTURE) | 10148
CHANNEL 7 RESERVED 2 (FUTURE) | 10069 | CHANNEL 15 RESERVED 2 (FUTURE) | 10149
CHANNEL 7 INHIBIT | 10070 | CHANNEL 15 INHIBIT | 10150
CHANNEL 8 A1 | 10071 | CHANNEL 16 A1 | 10151
CHANNEL 8 A2 | 10072 | CHANNEL 16 A2 | 10152
CHANNEL 8 A3 | 10073 | CHANNEL 16 A3 | 10153
CHANNEL 8 FAULT 1 (UNDER RANGE) | 10074 | CHANNEL 16 FAULT 1 (UNDER RANGE) | 10154
CHANNEL 8 FAULT 2 (UNDER RANGE) | 10075 | CHANNEL 16 FAULT 2 (UNDER RANGE) | 10155
CHANNEL 8 FAULT 3 (UNDER RANGE) | 10076 | CHANNEL 16 FAULT 3 (UNDER RANGE) | 10156
CHANNEL 8 FAULT 4 (UNDER RANGE) | 10077 | CHANNEL 16 FAULT 4 (UNDER RANGE) | 10157
CHANNEL 8 RESERVED 1 (FUTURE) | 10078 | CHANNEL 16 RESERVED 1 (FUTURE) | 10158
CHANNEL 8 RESERVED 2 (FUTURE) | 10079 | CHANNEL 16 RESERVED 2 (FUTURE) | 10159
CHANNEL 8 INHIBIT | 10080 | CHANNEL 16 INHIBIT | 10160
DISCRETE INPUT
DISCRETE INPUT STATUS | MODBUS ADDRESS
DISCRETE INPUT 1 ACTIVE (REMOTE RESET) | 10161
DISCRETE INPUT 2 ACTIVE (REMOTE SILENCE) | 10162
DISCRETE INPUT 3 ACTIVE | 10163
DISCRETE INPUT 4 ACTIVE | 10164
DISCRETE INPUT 5 ACTIVE | 10165
DISCRETE INPUT 6 ACTIVE | 10166
DISCRETE INPUT 7 ACTIVE | 10167
DISCRETE INPUT 8 ACTIVE | 10168
RELAY
RELAY STATUS | MODBUS ADDRESS
RELAY OUT 1 ACTIVE (COMMON ALARM) | 10201
RELAY OUT 2 ACTIVE (COMMON FAULT) | 10202
RELAY OUT 3 ACTIVE | 10203
RELAY OUT 4 ACTIVE | 10204
RELAY OUT 5 ACTIVE (PANEL BUZZER) | 10205
RELAY OUT 6 ACTIVE | 10206
RELAY OUT 7 ACTIVE | 10207
RELAY OUT 8 ACTIVE | 10208
RELAY OUT 9 ACTIVE | 10209
RELAY OUT 10 ACTIVE | 10210
RELAY OUT 11 ACTIVE | 10211
RELAY OUT 12 ACTIVE | 10212
RELAY OUT 13 ACTIVE | 10213
RELAY OUT 14 ACTIVE | 10214
RELAY OUT 15 ACTIVE | 10215
RELAY OUT 16 ACTIVE | 10216
RELAY OUT 17 ACTIVE | 10217
RELAY OUT 18 ACTIVE | 10218
RELAY OUT 19 ACTIVE | 10219
RELAY OUT 20 ACTIVE | 10220
RELAY OUT 21 ACTIVE | 10221
RELAY OUT 22 ACTIVE | 10222
RELAY OUT 23 ACTIVE | 10223
RELAY OUT 24 ACTIVE | 10224
RELAY OUT 25 ACTIVE | 10225
RELAY OUT 26 ACTIVE | 10226
RELAY OUT 27 ACTIVE | 10227
RELAY OUT 28 ACTIVE | 10228
RELAY OUT 29 ACTIVE | 10229
RELAY OUT 30 ACTIVE | 10230
RELAY OUT 31 ACTIVE | 10231
RELAY OUT 32 ACTIVE | 10232
RELAY OUT 33 ACTIVE | 10233
RELAY OUT 34 ACTIVE | 10234
RELAY OUT 35 ACTIVE | 10235
RELAY OUT 36 ACTIVE | 10236
RELAY OUT 37 ACTIVE | 10237
RELAY OUT 38 ACTIVE | 10238
RELAY OUT 39 ACTIVE | 10239
RELAY OUT 40 ACTIVE | 10240
RELAY OUT 41 ACTIVE | 10241
RELAY OUT 42 ACTIVE | 10242
RELAY OUT 43 ACTIVE | 10243
RELAY OUT 44 ACTIVE | 10244
RELAY OUT 45 ACTIVE | 10245
RELAY OUT 46 ACTIVE | 10246
RELAY OUT 47 ACTIVE | 10247
RELAY OUT 48 ACTIVE | 10248
RELAY OUT 49 ACTIVE | 10249
RELAY OUT 50 ACTIVE | 10250
RELAY OUT 51 ACTIVE | 10251
RELAY OUT 52 ACTIVE | 10252
RELAY OUT 53 ACTIVE | 10253
RELAY OUT 54 ACTIVE | 10254
RELAY OUT 55 ACTIVE | 10255
RELAY OUT 56 ACTIVE | 10256
VOTING ZONE
VOTING ZONE STATUS | MODBUS ADDRESS
ZONE ALARM 1 | 10301
ZONE ALARM 2 | 10302
ZONE ALARM 3 | 10303
ZONE ALARM 4 | 10304
ZONE ALARM 5 | 10305
ZONE ALARM 6 | 10306
ZONE ALARM 7 | 10307
ZONE ALARM 8 | 10308
ZONE ALARM 9 | 10309
ZONE ALARM 10 | 10310
ZONE ALARM 11 | 10311
ZONE ALARM 12 | 10312
SYSTEM FAULT
SYSTEM FAULTS | MODBUS ADDRESS
CPU BATTERY LOW WARNING | 10169
NO BATTERY (CPU) | 10170
CPU SD CARD MISSING | 10171
COMMUNICATION FAILURE WITH I/O MODULES | 10172
ANALOG
CHANNEL ANALOG VALUE | MODBUS ADDRESS
CHANNEL 1 | 40001
CHANNEL 2 | 40002
CHANNEL 3 | 40003
CHANNEL 4 | 40004
CHANNEL 5 | 40005
CHANNEL 6 | 40006
CHANNEL 7 | 40007
CHANNEL 8 | 40008
CHANNEL 9 | 40009
CHANNEL 10 | 40010
CHANNEL 11 | 40011
CHANNEL 12 | 40012
CHANNEL 13 | 40013
CHANNEL 14 | 40014
CHANNEL 15 | 40015
CHANNEL 16 | 40016